## Slide 1: CSCI 2930 Practical System Administration
Lecture 6: Infrastructure and Data Center Design

## Slide 2: Power Space and Cooling
Top three concerns for systems
Poor design will affect:
  System health
  Scalability
  Waste resources

## Slide 3: Power
Power supplies typically work over a range of volts
120v – Desktops
208v – Server/Network equipment and smaller HVAC
480v – HVAC Equipment / Data center feeds
Notes: Power factor 0.86

## Slide 4: Power
NEMA Connectors
  National Electrical Manufacturers Assoc.
  NEMA 5 rated for 125v
  NEMA 6 rated for 250v used for 208 and 240
    6-15, 6-20

## Slide 5: Power
NEMA Twist Lock Connectors
  NEMA L5 rated for 125v
    Single Pole
  NEMA L6 rated for 250v used for 208 and 240
    Two Pole
    L6-20, L6-30
  NEMA L21 120v/208v 3-phase

## Slide 6: Power
Single phase
  VA = Volt * Amps
  Watts = VA * 0.86
Three phase
  Watts = Sqrt(3) * 0.86 * V * A
Usage example:
  120v PSU running at 200Watts uses 1.93 amps
  208v PSU running at 200Watts uses 1.2 amps

## Slide 7: Power
Single phase
  VA = Volt * Amps
  Watts = V * A * 0.86
Three phase
  Watts = Sqrt(3) * 0.86 * V * A
Capacity Example – Customer needs 5000 Watts of power in one socket
  L6-30 two pole provides 5366 Watts across two breakers
  L21-30 three phase at 208v provides ~9300Watts

## Slide 8: Space
Racks
  Measured in Units (U)
    42U standard rack
  2 post
  4 post
  Standard server
  Tools
  Static load vs rolling

## Slide 9: Cooling
Server equipment has a large range of operating environment variables
Typical is to run temp between 68 and 72 deg F
Humidity should be between 40% and 50% non-condensing
  Too little humidity can cause static discharge and damage

## Slide 10: Cooling
CRAC units sold based on Tons of cooling capacity
1 KWatt = 3413 BTU
1 Ton = 12000 BTU = 3516 Watts
Too large a unit will cause
  Short cycling of the compressor(s)
  Inability to dehumidify

## Slide 11: Cooling
Air cooled
Chilled water
In Row

## Slide 12: Cooling
Hot aisle Cold aisle
  Servers take cold air in from the front
  Blow hot air out the back
  Arrange racks to provide proper flow
In Row More efficient if proper containment used

## Slide 13: Data Center Design
Raised floor
  Made up of solid and perforated tiles
  Provides cold air distribution
  Keeps equipment away from water leaks
  Tiles have different Static loads and dynamic loads
  Perforated tiles much lower max load

## Slide 14: Data Center Design
Grommets
  Seals air under raised floor
  Provides more efficient cooling

## Slide 15: Data Center Design
Cable Management:
  Proper cable management = Better airflow
  Large cable bundles can cause alien crosstalk
  Cable management trays
  Power cable interference with copper cables
    Always cross at right angles

## Slide 16: Data Center Design
Grounding/Bus bars
  Provide common ground for all equipment
  Helps to eliminate shorts and static build up

## Slide 17: Data Center Design
Water drains – Make sure water runs towards them…
Fire suppression
  Wet pipe (worst for data center)
    Water is in the pipe under pressure
  Dry pipe
    Water is not present until the system is activated
    Some delay but used in unheated areas
  Pre-action (good when accidental activation is undesirable)
    Similar to Dry pipe but requires a “preceding” fire detection event such as heat or smoke
  Gas (best for data center)
    Inert gas extinguishes the fire
    Suffocation can result…be aware of oxygen mask locations